{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["Implementation pivot","Implementation results","Implementation summary for web"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":2,"comments":0,"pivot_tables":1},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Implementation pivot","index":0,"n_rows":795,"n_cols":3,"rows_kept":795,"cut":false,"hidden":false,"merged":[]}
[]
[]
["building type","Data","Total"]
["hospital","Count of building size (ft2)",68]
[null,"Min of building size (ft2)2",29819]
[null,"Average of building size (ft2)3",218148.7794117647]
[null,"Max of building size (ft2)4",811821]
[null,"Min of annual electricity cost ($/ft2)",0.25703110448873162]
[null,"Average of annual electricity cost ($/ft2)2",1.3161896867287599]
[null,"Max of annual electricity cost ($/ft2)3",5.3294250882686027]
[null,"Min of annual fuel cost ($/ft2)",0.1651672129764222]
[null,"Average of annual fuel cost ($/ft2)2",1.2902436367815315]
[null,"Max of annual fuel cost ($/ft2)3",4.3701285723802545]
[null,"Min of annual energy cost ($/ft2)",0.51667786892547396]
[null,"Average of annual energy cost ($/ft2)2",2.606433323510291]
[null,"Max of annual energy cost ($/ft2)3",9.6995536606488564]
[null,"Min of annual electricity use (kWh/ft2)",3.5556779256116027]
[null,"Average of annual electricity use (kWh/ft2)2",19.412138247043341]
[null,"Max of annual electricity use (kWh/ft2)3",77.927160082606093]
[null,"Min of annual fuel use (MJ/ft2)",18.649999999999999]
[null,"Average of annual fuel use (MJ/ft2)2",117.42631312278638]
[null,"Max of annual fuel use (MJ/ft2)3",508.60035973619347]
[null,"Min of Total energy use (ekWh/ft2)",11.649197441386093]
[null,"Average of Total energy use (ekWh/ft2)2",52.030558558928448]
[null,"Max of Total energy use (ekWh/ft2)3",219.20503778710426]
[null,"Average of implementation cost ($/ft2)",0.26054171403835602]
[null,"Min of Savings as % of Total Electric Usage",0]
[null,"Average of Savings as % of Total Electric Usage2",4.1181213205640999E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.14813239854708757]
[null,"Min of Savings as % of Total Gas / Fuel Usage",4.9468216670789022E-3]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",9.066067212986173E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.31667184919519076]
[null,"Min of Savings as % of Total Energy Cost",6.7391355580504334E-3]
[null,"Average of Savings as % of Total Energy Cost2",6.6743117716519765E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.1703703999363711]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.8955882352941174]
["large hotel","Count of building size (ft2)",7]
[null,"Min of building size (ft2)2",150000]
[null,"Average of building size (ft2)3",338025.42857142858]
[null,"Max of building size (ft2)4",550000]
[null,"Min of annual electricity cost ($/ft2)",0.72627272727272729]
[null,"Average of annual electricity cost ($/ft2)2",1.2514461731001951]
[null,"Max of annual electricity cost ($/ft2)3",1.9523518518518519]
[null,"Min of annual fuel cost ($/ft2)",0.32241956521739129]
[null,"Average of annual fuel cost ($/ft2)2",0.72382946278382021]
[null,"Max of annual fuel cost ($/ft2)3",1.3758191269841269]
[null,"Min of annual energy cost ($/ft2)",1.46224]
[null,"Average of annual energy cost ($/ft2)2",1.9752756358840153]
[null,"Max of annual energy cost ($/ft2)3",3.3281709788359786]
[null,"Min of annual electricity use (kWh/ft2)",11.102008731970185]
[null,"Average of annual electricity use (kWh/ft2)2",19.970805654507359]
[null,"Max of annual electricity use (kWh/ft2)3",30.394179894179896]
[null,"Min of annual fuel use (MJ/ft2)",18.95]
[null,"Average of annual fuel use (MJ/ft2)2",38.660203624547144]
[null,"Max of annual fuel use (MJ/ft2)3",72.577777777777783]
[null,"Min of Total energy use (ekWh/ft2)",21.548698780702114]
[null,"Average of Total energy use (ekWh/ft2)2",30.709751105770462]
[null,"Max of Total energy use (ekWh/ft2)3",50.554673721340393]
[null,"Average of implementation cost ($/ft2)",0.21324879370805752]
[null,"Min of Savings as % of Total Electric Usage",2.0417405416933248E-2]
[null,"Average of Savings as % of Total Electric Usage2",4.4870162979035733E-2]
[null,"Max of Savings as % of Total Electric Usage3",6.9218649781477001E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",4.1769457323652059E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.10242690339383428]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.17795800977854473]
[null,"Min of Savings as % of Total Energy Cost",6.1060497993974491E-2]
[null,"Average of Savings as % of Total Energy Cost2",8.2685247299915096E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.10820267172086204]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.3714285714285714]
["large office","Count of building size (ft2)",68]
[null,"Min of building size (ft2)2",54055]
[null,"Average of building size (ft2)3",232280.84941176471]
[null,"Max of building size (ft2)4",659725]
[null,"Min of annual electricity cost ($/ft2)",0.66210857007735702]
[null,"Average of annual electricity cost ($/ft2)2",1.497566686325607]
[null,"Max of annual electricity cost ($/ft2)3",5.8173224478054832]
[null,"Min of annual fuel cost ($/ft2)",0]
[null,"Average of annual fuel cost ($/ft2)2",0.500832977095229]
[null,"Max of annual fuel cost ($/ft2)3",1.5774078684674104]
[null,"Min of annual energy cost ($/ft2)",0.86165595693645558]
[null,"Average of annual energy cost ($/ft2)2",1.9983996634208376]
[null,"Max of annual energy cost ($/ft2)3",6.0249962954309781]
[null,"Min of annual electricity use (kWh/ft2)",10.114865850862016]
[null,"Average of annual electricity use (kWh/ft2)2",23.626894666104956]
[null,"Max of annual electricity use (kWh/ft2)3",94.703123949675259]
[null,"Min of annual fuel use (MJ/ft2)",0]
[null,"Average of annual fuel use (MJ/ft2)2",41.720926662988632]
[null,"Max of annual fuel use (MJ/ft2)3",189.78978273634763]
[null,"Min of Total energy use (ekWh/ft2)",13.670750002005567]
[null,"Average of Total energy use (ekWh/ft2)2",35.216040961379576]
[null,"Max of Total energy use (ekWh/ft2)3",100.30036833458554]
[null,"Average of implementation cost ($/ft2)",0.26874653731093262]
[null,"Min of Savings as % of Total Electric Usage",1.3851578240429818E-3]
[null,"Average of Savings as % of Total Electric Usage2",4.5387547558809534E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.17878913847332015]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.13252478730527548]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.53364269141531318]
[null,"Min of Savings as % of Total Energy Cost",8.7111676346305553E-3]
[null,"Average of Savings as % of Total Energy Cost2",7.1152241661496529E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.27100000000000002]
[null,"Average of C.Op Project Simple Payback (with incentives)",2.2014705882352943]
["large school","Count of building size (ft2)",112]
[null,"Min of building size (ft2)2",50386]
[null,"Average of building size (ft2)3",108310.09355357142]
[null,"Max of building size (ft2)4",177348]
[null,"Min of annual electricity cost ($/ft2)",0.24998987179170476]
[null,"Average of annual electricity cost ($/ft2)2",0.62684275895712815]
[null,"Max of annual electricity cost ($/ft2)3",3.254813984226653]
[null,"Min of annual fuel cost ($/ft2)",8.3134068485200233E-2]
[null,"Average of annual fuel cost ($/ft2)2",0.4572687085322375]
[null,"Max of annual fuel cost ($/ft2)3",2.052551895224545]
[null,"Min of annual energy cost ($/ft2)",0.49436749769159744]
[null,"Average of annual energy cost ($/ft2)2",1.0841114674893653]
[null,"Max of annual energy cost ($/ft2)3",3.9975509349354734]
[null,"Min of annual electricity use (kWh/ft2)",3.1158008449237062]
[null,"Average of annual electricity use (kWh/ft2)2",7.3038790511964438]
[null,"Max of annual electricity use (kWh/ft2)3",32.502371310787638]
[null,"Min of annual fuel use (MJ/ft2)",9.3035403366221701]
[null,"Average of annual fuel use (MJ/ft2)2",41.471146824034903]
[null,"Max of annual fuel use (MJ/ft2)3",117.28867972711686]
[null,"Min of Total energy use (ekWh/ft2)",8.1045373388975701]
[null,"Average of Total energy use (ekWh/ft2)2",18.823642057872807]
[null,"Max of Total energy use (ekWh/ft2)3",65.082560123875652]
[null,"Average of implementation cost ($/ft2)",0.19371656975432722]
[null,"Min of Savings as % of Total Electric Usage",0]
[null,"Average of Savings as % of Total Electric Usage2",6.7142677024132819E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.25023512024721217]
[null,"Min of Savings as % of Total Gas / Fuel Usage",8.0188679245283018E-3]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.11551776452071758]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.49437416666666667]
[null,"Min of Savings as % of Total Energy Cost",4.0054839014576349E-3]
[null,"Average of Savings as % of Total Energy Cost2",9.8611174636920276E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.49793717006903193]
[null,"Average of C.Op Project Simple Payback (with incentives)",2.2178571428571439]
["medium office","Count of building size (ft2)",39]
[null,"Min of building size (ft2)2",46364]
[null,"Average of building size (ft2)3",74189.512820512828]
[null,"Max of building size (ft2)4",149194]
[null,"Min of annual electricity cost ($/ft2)",0.80895482263867491]
[null,"Average of annual electricity cost ($/ft2)2",1.5744488510973067]
[null,"Max of annual electricity cost ($/ft2)3",6.7244979379046175]
[null,"Min of annual fuel cost ($/ft2)",0]
[null,"Average of annual fuel cost ($/ft2)2",0.3433795262494424]
[null,"Max of annual fuel cost ($/ft2)3",1.5046837529653174]
[null,"Min of annual energy cost ($/ft2)",0.99474005960416723]
[null,"Average of annual energy cost ($/ft2)2",1.917828377346749]
[null,"Max of annual energy cost ($/ft2)3",7.0513002826967561]
[null,"Min of annual electricity use (kWh/ft2)",9.2972643439751099]
[null,"Average of annual electricity use (kWh/ft2)2",21.501953405975428]
[null,"Max of annual electricity use (kWh/ft2)3",97.496836488686014]
[null,"Min of annual fuel use (MJ/ft2)",0]
[null,"Average of annual fuel use (MJ/ft2)2",27.767388597213564]
[null,"Max of annual fuel use (MJ/ft2)3",97.327539001637618]
[null,"Min of Total energy use (ekWh/ft2)",14.687785674056338]
[null,"Average of Total energy use (ekWh/ft2)2",29.21511690520143]
[null,"Max of Total energy use (ekWh/ft2)3",109.20787933920482]
[null,"Average of implementation cost ($/ft2)",0.31090854177307403]
[null,"Min of Savings as % of Total Electric Usage",1.0929025751543897E-2]
[null,"Average of Savings as % of Total Electric Usage2",6.9194661685312575E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.1820978465813238]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.12182506664533342]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.43228269875004499]
[null,"Min of Savings as % of Total Energy Cost",1.3828812926753897E-2]
[null,"Average of Savings as % of Total Energy Cost2",9.8895845326325116E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.26393303770524174]
[null,"Average of C.Op Project Simple Payback (with incentives)",2.2256410256410257]
["Recreation","Count of building size (ft2)",22]
[null,"Min of building size (ft2)2",49000]
[null,"Average of building size (ft2)3",115913.81818181818]
[null,"Max of building size (ft2)4",512000]
[null,"Min of annual electricity cost ($/ft2)",0.41265327866206053]
[null,"Average of annual electricity cost ($/ft2)2",1.8768337481078115]
[null,"Max of annual electricity cost ($/ft2)3",3.9490348817228935]
[null,"Min of annual fuel cost ($/ft2)",0.34751400489224038]
[null,"Average of annual fuel cost ($/ft2)2",1.3113707595994506]
[null,"Max of annual fuel cost ($/ft2)3",3.8222277227722774]
[null,"Min of annual energy cost ($/ft2)",0.76016728355430097]
[null,"Average of annual energy cost ($/ft2)2",3.1882045077072623]
[null,"Max of annual energy cost ($/ft2)3",7.6340099009900992]
[null,"Min of annual electricity use (kWh/ft2)",7.722448979591837]
[null,"Average of annual electricity use (kWh/ft2)2",25.232783731390807]
[null,"Max of annual electricity use (kWh/ft2)3",49.335726072607258]
[null,"Min of annual fuel use (MJ/ft2)",26.423705472508313]
[null,"Average of annual fuel use (MJ/ft2)2",117.4221838749787]
[null,"Max of annual fuel use (MJ/ft2)3",355.49504950495049]
[null,"Min of Total energy use (ekWh/ft2)",15.412110095889968]
[null,"Average of Total energy use (ekWh/ft2)2",57.850057029995995]
[null,"Max of Total energy use (ekWh/ft2)3",148.08435093509354]
[null,"Average of implementation cost ($/ft2)",0.50261072004780472]
[null,"Min of Savings as % of Total Electric Usage",0]
[null,"Average of Savings as % of Total Electric Usage2",6.0748782367188413E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.23375688630736027]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.10276263421098628]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.47481000000000001]
[null,"Min of Savings as % of Total Energy Cost",0]
[null,"Average of Savings as % of Total Energy Cost2",8.9344412290834396E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.36443609674315791]
[null,"Average of C.Op Project Simple Payback (with incentives)",2.4999999999999996]
["restaurant","Count of building size (ft2)",3]
[null,"Min of building size (ft2)2",26302]
[null,"Average of building size (ft2)3",34962.333333333336]
[null,"Max of building size (ft2)4",50000]
[null,"Min of annual electricity cost ($/ft2)",1.5543158999475248]
[null,"Average of annual electricity cost ($/ft2)2",3.2160441007340359]
[null,"Max of annual electricity cost ($/ft2)3",5.4346399999999999]
[null,"Min of annual fuel cost ($/ft2)",0]
[null,"Average of annual fuel cost ($/ft2)2",0.78699721182438331]
[null,"Max of annual fuel cost ($/ft2)3",1.2065399999999999]
[null,"Min of annual energy cost ($/ft2)",2.6591764022545816]
[null,"Average of annual energy cost ($/ft2)2",4.0030413125584188]
[null,"Max of annual energy cost ($/ft2)3",6.6411800000000003]
[null,"Min of annual electricity use (kWh/ft2)",17.270176666083611]
[null,"Average of annual electricity use (kWh/ft2)2",43.637310328002066]
[null,"Max of annual electricity use (kWh/ft2)3",75.65352]
[null,"Min of annual fuel use (MJ/ft2)",0]
[null,"Average of annual fuel use (MJ/ft2)2",54.788387849105014]
[null,"Max of annual fuel use (MJ/ft2)3",115.44516354731502]
[null,"Min of Total energy use (ekWh/ft2)",37.98823431792259]
[null,"Average of Total energy use (ekWh/ft2)2",58.856306952753449]
[null,"Max of Total energy use (ekWh/ft2)3",89.242408888888875]
[null,"Average of implementation cost ($/ft2)",0.28203225313588004]
[null,"Min of Savings as % of Total Electric Usage",1.4635778883187575E-2]
[null,"Average of Savings as % of Total Electric Usage2",6.7494114295125487E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.14631795152455052]
[null,"Min of Savings as % of Total Gas / Fuel Usage",1.9116523272727275E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",3.7600593166513888E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",5.6084663060300494E-2]
[null,"Min of Savings as % of Total Energy Cost",1.7047803038958764E-2]
[null,"Average of Savings as % of Total Energy Cost2",5.1891627399843571E-2]
[null,"Max of Savings as % of Total Energy Cost3",8.6487906194896949E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.8666666666666665]
["shopping mall","Count of building size (ft2)",3]
[null,"Min of building size (ft2)2",250000]
[null,"Average of building size (ft2)3",375333.33333333331]
[null,"Max of building size (ft2)4",576000]
[null,"Min of annual electricity cost ($/ft2)",0.49362193333333332]
[null,"Average of annual electricity cost ($/ft2)2",1.2368783666666667]
[null,"Max of annual electricity cost ($/ft2)3",1.8791720000000001]
[null,"Min of annual fuel cost ($/ft2)",6.3236666666666663E-2]
[null,"Average of annual fuel cost ($/ft2)2",0.15052200314113692]
[null,"Max of annual fuel cost ($/ft2)3",0.29368534275674413]
[null,"Min of annual energy cost ($/ft2)",0.55685859999999998]
[null,"Average of annual energy cost ($/ft2)2",1.3874003698078037]
[null,"Max of annual energy cost ($/ft2)3",1.973816]
[null,"Min of annual electricity use (kWh/ft2)",8.472461233333334]
[null,"Average of annual electricity use (kWh/ft2)2",22.715824855555553]
[null,"Max of annual electricity use (kWh/ft2)3",33.996679999999998]
[null,"Min of annual fuel use (MJ/ft2)",5.0933333333333337]
[null,"Average of annual fuel use (MJ/ft2)2",75.066203703703692]
[null,"Max of annual fuel use (MJ/ft2)3",187.64]
[null,"Min of Total energy use (ekWh/ft2)",9.8872760481481485]
[null,"Average of Total energy use (ekWh/ft2)2",43.567548106584354]
[null,"Max of Total energy use (ekWh/ft2)3",86.118902222222218]
[null,"Average of implementation cost ($/ft2)",7.914969185349667E-2]
[null,"Min of Savings as % of Total Electric Usage",1.955982884268704E-2]
[null,"Average of Savings as % of Total Electric Usage2",3.1647526624582124E-2]
[null,"Max of Savings as % of Total Electric Usage3",3.8362625879938869E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",1.4618538324420678E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",4.3855614973262035E-2]
[null,"Min of Savings as % of Total Energy Cost",2.0585857518593566E-2]
[null,"Average of Savings as % of Total Energy Cost2",2.4277620426981908E-2]
[null,"Max of Savings as % of Total Energy Cost3",2.8672440149822603E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.4333333333333333]
["univ. / college","Count of building size (ft2)",133]
[null,"Min of building size (ft2)2",29637]
[null,"Average of building size (ft2)3",124740.87614736841]
[null,"Max of building size (ft2)4",580347]
[null,"Min of annual electricity cost ($/ft2)",0.22650623381709784]
[null,"Average of annual electricity cost ($/ft2)2",1.0236844516386217]
[null,"Max of annual electricity cost ($/ft2)3",4.1744033959470714]
[null,"Min of annual fuel cost ($/ft2)",0]
[null,"Average of annual fuel cost ($/ft2)2",0.57404537935523003]
[null,"Max of annual fuel cost ($/ft2)3",2.4616655376898207]
[null,"Min of annual energy cost ($/ft2)",0.44685437641504888]
[null,"Average of annual energy cost ($/ft2)2",1.597729830993851]
[null,"Max of annual energy cost ($/ft2)3",4.8175907980938284]
[null,"Min of annual electricity use (kWh/ft2)",4.9478380519534673]
[null,"Average of annual electricity use (kWh/ft2)2",17.081806830587105]
[null,"Max of annual electricity use (kWh/ft2)3",59.634334227815302]
[null,"Min of annual fuel use (MJ/ft2)",0]
[null,"Average of annual fuel use (MJ/ft2)2",58.505537135849416]
[null,"Max of annual fuel use (MJ/ft2)3",289.93823800847156]
[null,"Min of Total energy use (ekWh/ft2)",6.7451425183894695]
[null,"Average of Total energy use (ekWh/ft2)2",33.333344923878606]
[null,"Max of Total energy use (ekWh/ft2)3",105.21072022819941]
[null,"Average of implementation cost ($/ft2)",0.34412509051723644]
[null,"Min of Savings as % of Total Electric Usage",5.857102922350205E-4]
[null,"Average of Savings as % of Total Electric Usage2",8.5382540256367837E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.32264004247707534]
[null,"Min of Savings as % of Total Gas / Fuel Usage",-6.2473091989838712E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.16731591849176014]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.78629032286453093]
[null,"Min of Savings as % of Total Energy Cost",1.1677322430375107E-2]
[null,"Average of Savings as % of Total Energy Cost2",0.13606124611834766]
[null,"Max of Savings as % of Total Energy Cost3",0.38363098324392464]
[null,"Average of C.Op Project Simple Payback (with incentives)",2.1045112781954884]
["extended care","Count of building size (ft2)",15]
[null,"Min of building size (ft2)2",40181]
[null,"Average of building size (ft2)3",71593.53333333334]
[null,"Max of building size (ft2)4",185656]
[null,"Min of annual electricity cost ($/ft2)",0.65666298322291217]
[null,"Average of annual electricity cost ($/ft2)2",1.024847848418913]
[null,"Max of annual electricity cost ($/ft2)3",1.5754390872579775]
[null,"Min of annual fuel cost ($/ft2)",0.15297620236977241]
[null,"Average of annual fuel cost ($/ft2)2",1.1819809512039514]
[null,"Max of annual fuel cost ($/ft2)3",2.5013065876906997]
[null,"Min of annual energy cost ($/ft2)",1.5870769230769231]
[null,"Average of annual energy cost ($/ft2)2",2.2068287996228642]
[null,"Max of annual energy cost ($/ft2)3",3.3657698912421292]
[null,"Min of annual electricity use (kWh/ft2)",10.692307692307692]
[null,"Average of annual electricity use (kWh/ft2)2",16.058308162483705]
[null,"Max of annual electricity use (kWh/ft2)3",43.051012048674245]
[null,"Min of annual fuel use (MJ/ft2)",7.1332947029791995]
[null,"Average of annual fuel use (MJ/ft2)2",107.48426744466643]
[null,"Max of annual fuel use (MJ/ft2)3",159.42858564993404]
[null,"Min of Total energy use (ekWh/ft2)",30.295353335723028]
[null,"Average of Total energy use (ekWh/ft2)2",45.915049119335478]
[null,"Max of Total energy use (ekWh/ft2)3",58.2]
[null,"Average of implementation cost ($/ft2)",0.43322526956889135]
[null,"Min of Savings as % of Total Electric Usage",2.3621137741842335E-3]
[null,"Average of Savings as % of Total Electric Usage2",5.2471666464693929E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.11900740332391782]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.11729995854328325]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.29441857828168888]
[null,"Min of Savings as % of Total Energy Cost",1.3534824673545005E-2]
[null,"Average of Savings as % of Total Energy Cost2",0.10022053429546232]
[null,"Max of Savings as % of Total Energy Cost3",0.20685405792956582]
[null,"Average of C.Op Project Simple Payback (with incentives)",2.6333333333333333]
["large non-food retail","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",113975]
[null,"Average of building size (ft2)3",113975]
[null,"Max of building size (ft2)4",113975]
[null,"Min of annual electricity cost ($/ft2)",1.7620370256635227]
[null,"Average of annual electricity cost ($/ft2)2",1.7620370256635227]
[null,"Max of annual electricity cost ($/ft2)3",1.7620370256635227]
[null,"Min of annual fuel cost ($/ft2)",0.173105593331871]
[null,"Average of annual fuel cost ($/ft2)2",0.173105593331871]
[null,"Max of annual fuel cost ($/ft2)3",0.173105593331871]
[null,"Min of annual energy cost ($/ft2)",1.9351426189953937]
[null,"Average of annual energy cost ($/ft2)2",1.9351426189953937]
[null,"Max of annual energy cost ($/ft2)3",1.9351426189953937]
[null,"Min of annual electricity use (kWh/ft2)",27.919806975213863]
[null,"Average of annual electricity use (kWh/ft2)2",27.919806975213863]
[null,"Max of annual electricity use (kWh/ft2)3",27.919806975213863]
[null,"Min of annual fuel use (MJ/ft2)",16.360078964685236]
[null,"Average of annual fuel use (MJ/ft2)2",16.360078964685236]
[null,"Max of annual fuel use (MJ/ft2)3",16.360078964685236]
[null,"Min of Total energy use (ekWh/ft2)",32.464273354293098]
[null,"Average of Total energy use (ekWh/ft2)2",32.464273354293098]
[null,"Max of Total energy use (ekWh/ft2)3",32.464273354293098]
[null,"Average of implementation cost ($/ft2)",0.13487763529667465]
[null,"Min of Savings as % of Total Electric Usage",5.9979070819820499E-2]
[null,"Average of Savings as % of Total Electric Usage2",5.9979070819820499E-2]
[null,"Max of Savings as % of Total Electric Usage3",5.9979070819820499E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",4.5048910245409302E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",4.5048910245409302E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",4.5048910245409302E-2]
[null,"Min of Savings as % of Total Energy Cost",8.5430502319067347E-2]
[null,"Average of Savings as % of Total Energy Cost2",8.5430502319067347E-2]
[null,"Max of Savings as % of Total Energy Cost3",8.5430502319067347E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.8]
["museum","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",311803]
[null,"Average of building size (ft2)3",311803]
[null,"Max of building size (ft2)4",311803]
[null,"Min of annual electricity cost ($/ft2)",1.0423248012366784]
[null,"Average of annual electricity cost ($/ft2)2",1.0423248012366784]
[null,"Max of annual electricity cost ($/ft2)3",1.0423248012366784]
[null,"Min of annual fuel cost ($/ft2)",0]
[null,"Average of annual fuel cost ($/ft2)2",0]
[null,"Max of annual fuel cost ($/ft2)3",0]
[null,"Min of annual energy cost ($/ft2)",1.0423248012366784]
[null,"Average of annual energy cost ($/ft2)2",1.0423248012366784]
[null,"Max of annual energy cost ($/ft2)3",1.0423248012366784]
[null,"Min of annual electricity use (kWh/ft2)",19.082561745717648]
[null,"Average of annual electricity use (kWh/ft2)2",19.082561745717648]
[null,"Max of annual electricity use (kWh/ft2)3",19.082561745717648]
[null,"Min of annual fuel use (MJ/ft2)",0]
[null,"Average of annual fuel use (MJ/ft2)2",0]
[null,"Max of annual fuel use (MJ/ft2)3",0]
[null,"Min of Total energy use (ekWh/ft2)",19.082561745717648]
[null,"Average of Total energy use (ekWh/ft2)2",19.082561745717648]
[null,"Max of Total energy use (ekWh/ft2)3",19.082561745717648]
[null,"Average of implementation cost ($/ft2)",0.31818249999999998]
[null,"Min of Savings as % of Total Electric Usage",8.9120039976558943E-2]
[null,"Average of Savings as % of Total Electric Usage2",8.9120039976558943E-2]
[null,"Max of Savings as % of Total Electric Usage3",8.9120039976558943E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0]
[null,"Min of Savings as % of Total Energy Cost",9.6719576000000002E-2]
[null,"Average of Savings as % of Total Energy Cost2",9.6719576000000002E-2]
[null,"Max of Savings as % of Total Energy Cost3",9.6719576000000002E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",2.2000000000000002]
["Food retail (e.g. supermarkets, grocery stores)","Count of building size (ft2)",21]
[null,"Min of building size (ft2)2",102024]
[null,"Average of building size (ft2)3",133211.33333333334]
[null,"Max of building size (ft2)4",155623]
[null,"Min of annual electricity cost ($/ft2)",0.58202258471212664]
[null,"Average of annual electricity cost ($/ft2)2",2.5517098353783112]
[null,"Max of annual electricity cost ($/ft2)3",3.8551166097633156]
[null,"Min of annual fuel cost ($/ft2)",0.11184343237816551]
[null,"Average of annual fuel cost ($/ft2)2",0.42267326578840808]
[null,"Max of annual fuel cost ($/ft2)3",0.79503260243701268]
[null,"Min of annual energy cost ($/ft2)",0.69386601709029216]
[null,"Average of annual energy cost ($/ft2)2",2.9743831011667199]
[null,"Max of annual energy cost ($/ft2)3",4.2181479583366412]
[null,"Min of annual electricity use (kWh/ft2)",6.0936697433343188]
[null,"Average of annual electricity use (kWh/ft2)2",39.48515599516486]
[null,"Max of annual electricity use (kWh/ft2)3",70.784400060632748]
[null,"Min of annual fuel use (MJ/ft2)",11.302862390461812]
[null,"Average of annual fuel use (MJ/ft2)2",44.293254024780978]
[null,"Max of annual fuel use (MJ/ft2)3",78.368168367912546]
[null,"Min of Total energy use (ekWh/ft2)",9.2333537406848212]
[null,"Average of Total energy use (ekWh/ft2)2",51.788837668715132]
[null,"Max of Total energy use (ekWh/ft2)3",80.372554539395651]
[null,"Average of implementation cost ($/ft2)",2.4078703681816103E-2]
[null,"Min of Savings as % of Total Electric Usage",1.1463821413195763E-2]
[null,"Average of Savings as % of Total Electric Usage2",5.6274064732305111E-2]
[null,"Max of Savings as % of Total Electric Usage3",0.16130808062893404]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",3.0772190475604443E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.13191723758047302]
[null,"Min of Savings as % of Total Energy Cost",2.4560292708493744E-2]
[null,"Average of Savings as % of Total Energy Cost2",7.4583924237362528E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.20070255100939305]
[null,"Average of C.Op Project Simple Payback (with incentives)",0.23809523809523814]
["public aquarium","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",165000]
[null,"Average of building size (ft2)3",165000]
[null,"Max of building size (ft2)4",165000]
[null,"Min of annual electricity cost ($/ft2)",3.5696303030303032]
[null,"Average of annual electricity cost ($/ft2)2",3.5696303030303032]
[null,"Max of annual electricity cost ($/ft2)3",3.5696303030303032]
[null,"Min of annual fuel cost ($/ft2)",0.64654545454545453]
[null,"Average of annual fuel cost ($/ft2)2",0.64654545454545453]
[null,"Max of annual fuel cost ($/ft2)3",0.64654545454545453]
[null,"Min of annual energy cost ($/ft2)",4.2161757575757575]
[null,"Average of annual energy cost ($/ft2)2",4.2161757575757575]
[null,"Max of annual energy cost ($/ft2)3",4.2161757575757575]
[null,"Min of annual electricity use (kWh/ft2)",55.502636363636363]
[null,"Average of annual electricity use (kWh/ft2)2",55.502636363636363]
[null,"Max of annual electricity use (kWh/ft2)3",55.502636363636363]
[null,"Min of annual fuel use (MJ/ft2)",82.060606060606062]
[null,"Average of annual fuel use (MJ/ft2)2",82.060606060606062]
[null,"Max of annual fuel use (MJ/ft2)3",82.060606060606062]
[null,"Min of Total energy use (ekWh/ft2)",78.297249158249159]
[null,"Average of Total energy use (ekWh/ft2)2",78.297249158249159]
[null,"Max of Total energy use (ekWh/ft2)3",78.297249158249159]
[null,"Average of implementation cost ($/ft2)",0.18938931818181817]
[null,"Min of Savings as % of Total Electric Usage",4.0690395815213805E-3]
[null,"Average of Savings as % of Total Electric Usage2",4.0690395815213805E-3]
[null,"Max of Savings as % of Total Electric Usage3",4.0690395815213805E-3]
[null,"Min of Savings as % of Total Gas / Fuel Usage",1.9202363367799114E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",1.9202363367799114E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",1.9202363367799114E-2]
[null,"Min of Savings as % of Total Energy Cost",7.5653352062160844E-3]
[null,"Average of Savings as % of Total Energy Cost2",7.5653352062160844E-3]
[null,"Max of Savings as % of Total Energy Cost3",7.5653352062160844E-3]
[null,"Average of C.Op Project Simple Payback (with incentives)",7.5]
["airport terminal","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",157000]
[null,"Average of building size (ft2)3",157000]
[null,"Max of building size (ft2)4",157000]
[null,"Min of annual electricity cost ($/ft2)",1.6992165605095542]
[null,"Average of annual electricity cost ($/ft2)2",1.6992165605095542]
[null,"Max of annual electricity cost ($/ft2)3",1.6992165605095542]
[null,"Min of annual fuel cost ($/ft2)",0.80860509554140125]
[null,"Average of annual fuel cost ($/ft2)2",0.80860509554140125]
[null,"Max of annual fuel cost ($/ft2)3",0.80860509554140125]
[null,"Min of annual energy cost ($/ft2)",2.5078216560509556]
[null,"Average of annual energy cost ($/ft2)2",2.5078216560509556]
[null,"Max of annual energy cost ($/ft2)3",2.5078216560509556]
[null,"Min of annual electricity use (kWh/ft2)",25.979044585987261]
[null,"Average of annual electricity use (kWh/ft2)2",25.979044585987261]
[null,"Max of annual electricity use (kWh/ft2)3",25.979044585987261]
[null,"Min of annual fuel use (MJ/ft2)",52.159235668789812]
[null,"Average of annual fuel use (MJ/ft2)2",52.159235668789812]
[null,"Max of annual fuel use (MJ/ft2)3",52.159235668789812]
[null,"Min of Total energy use (ekWh/ft2)",40.467721160651095]
[null,"Average of Total energy use (ekWh/ft2)2",40.467721160651095]
[null,"Max of Total energy use (ekWh/ft2)3",40.467721160651095]
[null,"Average of implementation cost ($/ft2)",0.30762854792266559]
[null,"Min of Savings as % of Total Electric Usage",2.2997467336486291E-2]
[null,"Average of Savings as % of Total Electric Usage2",2.2997467336486291E-2]
[null,"Max of Savings as % of Total Electric Usage3",2.2997467336486291E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0.1257784833312981]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.1257784833312981]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.1257784833312981]
[null,"Min of Savings as % of Total Energy Cost",6.1492495421691176E-2]
[null,"Average of Savings as % of Total Energy Cost2",6.1492495421691176E-2]
[null,"Max of Savings as % of Total Energy Cost3",6.1492495421691176E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",2]
["Residential","Count of building size (ft2)",2]
[null,"Min of building size (ft2)2",59395]
[null,"Average of building size (ft2)3",65832]
[null,"Max of building size (ft2)4",72269]
[null,"Min of annual electricity cost ($/ft2)",0.78818027093221155]
[null,"Average of annual electricity cost ($/ft2)2",0.87706008243133859]
[null,"Max of annual electricity cost ($/ft2)3",0.96593989393046553]
[null,"Min of annual fuel cost ($/ft2)",5.3231676099018944E-2]
[null,"Average of annual fuel cost ($/ft2)2",8.687032075007349E-2]
[null,"Max of annual fuel cost ($/ft2)3",0.12050896540112803]
[null,"Min of annual energy cost ($/ft2)",0.84141194703123046]
[null,"Average of annual energy cost ($/ft2)2",0.96393040318141199]
[null,"Max of annual energy cost ($/ft2)3",1.0864488593315935]
[null,"Min of annual electricity use (kWh/ft2)",11.143367142204818]
[null,"Average of annual electricity use (kWh/ft2)2",11.53430668752635]
[null,"Max of annual electricity use (kWh/ft2)3",11.925246232847883]
[null,"Min of annual fuel use (MJ/ft2)",8.8696398179025593]
[null,"Average of annual fuel use (MJ/ft2)2",10.646622249215611]
[null,"Max of annual fuel use (MJ/ft2)3",12.423604680528664]
[null,"Min of Total energy use (ekWh/ft2)",13.607155980511084]
[null,"Average of Total energy use (ekWh/ft2)2",14.49170175675291]
[null,"Max of Total energy use (ekWh/ft2)3",15.376247532994734]
[null,"Average of implementation cost ($/ft2)",6.9220312764691455E-2]
[null,"Min of Savings as % of Total Electric Usage",3.4834109840463083E-2]
[null,"Average of Savings as % of Total Electric Usage2",4.0172605508817447E-2]
[null,"Max of Savings as % of Total Electric Usage3",4.551110117717181E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0]
[null,"Min of Savings as % of Total Energy Cost",3.3602960453980604E-2]
[null,"Average of Savings as % of Total Energy Cost2",4.3287083560433259E-2]
[null,"Max of Savings as % of Total Energy Cost3",5.2971206666885914E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.65]
["Large Commerical Bldg","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",318320]
[null,"Average of building size (ft2)3",318320]
[null,"Max of building size (ft2)4",318320]
[null,"Min of annual electricity cost ($/ft2)",1.1409682080924854]
[null,"Average of annual electricity cost ($/ft2)2",1.1409682080924854]
[null,"Max of annual electricity cost ($/ft2)3",1.1409682080924854]
[null,"Min of annual fuel cost ($/ft2)",0.15537823573762252]
[null,"Average of annual fuel cost ($/ft2)2",0.15537823573762252]
[null,"Max of annual fuel cost ($/ft2)3",0.15537823573762252]
[null,"Min of annual energy cost ($/ft2)",1.296346443830108]
[null,"Average of annual energy cost ($/ft2)2",1.296346443830108]
[null,"Max of annual energy cost ($/ft2)3",1.296346443830108]
[null,"Min of annual electricity use (kWh/ft2)",14.814978637848705]
[null,"Average of annual electricity use (kWh/ft2)2",14.814978637848705]
[null,"Max of annual electricity use (kWh/ft2)3",14.814978637848705]
[null,"Min of annual fuel use (MJ/ft2)",28.55302839909525]
[null,"Average of annual fuel use (MJ/ft2)2",28.55302839909525]
[null,"Max of annual fuel use (MJ/ft2)3",28.55302839909525]
[null,"Min of Total energy use (ekWh/ft2)",22.746375415375162]
[null,"Average of Total energy use (ekWh/ft2)2",22.746375415375162]
[null,"Max of Total energy use (ekWh/ft2)3",22.746375415375162]
[null,"Average of implementation cost ($/ft2)",7.2727285018929153E-2]
[null,"Min of Savings as % of Total Electric Usage",1.1344591832234076E-2]
[null,"Average of Savings as % of Total Electric Usage2",1.1344591832234076E-2]
[null,"Max of Savings as % of Total Electric Usage3",1.1344591832234076E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0.1936413246781824]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.1936413246781824]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.1936413246781824]
[null,"Min of Savings as % of Total Energy Cost",3.6906200978659799E-2]
[null,"Average of Savings as % of Total Energy Cost2",3.6906200978659799E-2]
[null,"Max of Savings as % of Total Energy Cost3",3.6906200978659799E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.5]
["works yard","Count of building size (ft2)",2]
[null,"Min of building size (ft2)2",110320]
[null,"Average of building size (ft2)3",152150.64000000001]
[null,"Max of building size (ft2)4",193981.28]
[null,"Min of annual electricity cost ($/ft2)",0.75445975344452498]
[null,"Average of annual electricity cost ($/ft2)2",0.86696785556228251]
[null,"Max of annual electricity cost ($/ft2)3",0.97947595768004003]
[null,"Min of annual fuel cost ($/ft2)",0.58288614938361127]
[null,"Average of annual fuel cost ($/ft2)2",0.83015485141582768]
[null,"Max of annual fuel cost ($/ft2)3",1.0774235534480441]
[null,"Min of annual energy cost ($/ft2)",1.3373459028281363]
[null,"Average of annual energy cost ($/ft2)2",1.6971227069781103]
[null,"Max of annual energy cost ($/ft2)3",2.0568995111280843]
[null,"Min of annual electricity use (kWh/ft2)",11.176740391588107]
[null,"Average of annual electricity use (kWh/ft2)2",12.522550906427576]
[null,"Max of annual electricity use (kWh/ft2)3",13.868361421267043]
[null,"Min of annual fuel use (MJ/ft2)",48.712835387962294]
[null,"Average of annual fuel use (MJ/ft2)2",69.82730024512216]
[null,"Max of annual fuel use (MJ/ft2)3",90.941765102282034]
[null,"Min of Total energy use (ekWh/ft2)",24.708083554910967]
[null,"Average of Total energy use (ekWh/ft2)2",31.919023196739289]
[null,"Max of Total energy use (ekWh/ft2)3",39.129962838567607]
[null,"Average of implementation cost ($/ft2)",0.24531377957105033]
[null,"Min of Savings as % of Total Electric Usage",3.7989705235944131E-2]
[null,"Average of Savings as % of Total Electric Usage2",4.004077408870485E-2]
[null,"Max of Savings as % of Total Electric Usage3",4.2091842941465576E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0.23581429624170966]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.28351935504307291]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.33122441384443618]
[null,"Min of Savings as % of Total Energy Cost",0.14603266895869005]
[null,"Average of Savings as % of Total Energy Cost2",0.16065693137722969]
[null,"Max of Savings as % of Total Energy Cost3",0.17528119379576931]
[null,"Average of C.Op Project Simple Payback (with incentives)",0.95]
["Medium non-food retail","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",128138]
[null,"Average of building size (ft2)3",128138]
[null,"Max of building size (ft2)4",128138]
[null,"Min of annual electricity cost ($/ft2)",0.25329722642775759]
[null,"Average of annual electricity cost ($/ft2)2",0.25329722642775759]
[null,"Max of annual electricity cost ($/ft2)3",0.25329722642775759]
[null,"Min of annual fuel cost ($/ft2)",0.1813435514835568]
[null,"Average of annual fuel cost ($/ft2)2",0.1813435514835568]
[null,"Max of annual fuel cost ($/ft2)3",0.1813435514835568]
[null,"Min of annual energy cost ($/ft2)",0.43464077791131439]
[null,"Average of annual energy cost ($/ft2)2",0.43464077791131439]
[null,"Max of annual energy cost ($/ft2)3",0.43464077791131439]
[null,"Min of annual electricity use (kWh/ft2)",3.1904665282742042]
[null,"Average of annual electricity use (kWh/ft2)2",3.1904665282742042]
[null,"Max of annual electricity use (kWh/ft2)3",3.1904665282742042]
[null,"Min of annual fuel use (MJ/ft2)",19.120011237884157]
[null,"Average of annual fuel use (MJ/ft2)2",19.120011237884157]
[null,"Max of annual fuel use (MJ/ft2)3",19.120011237884157]
[null,"Min of Total energy use (ekWh/ft2)",8.5015807610198024]
[null,"Average of Total energy use (ekWh/ft2)2",8.5015807610198024]
[null,"Max of Total energy use (ekWh/ft2)3",8.5015807610198024]
[null,"Average of implementation cost ($/ft2)",2.6180478115799797E-2]
[null,"Min of Savings as % of Total Electric Usage",2.1157477618511816E-2]
[null,"Average of Savings as % of Total Electric Usage2",2.1157477618511816E-2]
[null,"Max of Savings as % of Total Electric Usage3",2.1157477618511816E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",3.0183673469387756E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",3.0183673469387756E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",3.0183673469387756E-2]
[null,"Min of Savings as % of Total Energy Cost",2.6242469860454681E-2]
[null,"Average of Savings as % of Total Energy Cost2",2.6242469860454681E-2]
[null,"Max of Savings as % of Total Energy Cost3",2.6242469860454681E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",0.9]
["Movie Theatre / Theatre","Count of building size (ft2)",6]
[null,"Min of building size (ft2)2",54004]
[null,"Average of building size (ft2)3",101283.66666666667]
[null,"Max of building size (ft2)4",140080]
[null,"Min of annual electricity cost ($/ft2)",0.77163668067226898]
[null,"Average of annual electricity cost ($/ft2)2",1.7068348968676357]
[null,"Max of annual electricity cost ($/ft2)3",2.2919660678642715]
[null,"Min of annual fuel cost ($/ft2)",0.10780682912376861]
[null,"Average of annual fuel cost ($/ft2)2",0.40534313756814949]
[null,"Max of annual fuel cost ($/ft2)3",1.0031576242147344]
[null,"Min of annual energy cost ($/ft2)",1.1519325630252102]
[null,"Average of annual energy cost ($/ft2)2",2.1121780344357854]
[null,"Max of annual energy cost ($/ft2)3",2.7545109780439123]
[null,"Min of annual electricity use (kWh/ft2)",8.7403361344537807]
[null,"Average of annual electricity use (kWh/ft2)2",20.724608060134464]
[null,"Max of annual electricity use (kWh/ft2)3",28.140079840319363]
[null,"Min of annual fuel use (MJ/ft2)",10.988074957410563]
[null,"Average of annual fuel use (MJ/ft2)2",33.659723789774304]
[null,"Max of annual fuel use (MJ/ft2)3",65.120876754362797]
[null,"Min of Total energy use (ekWh/ft2)",18.000723622782445]
[null,"Average of Total energy use (ekWh/ft2)2",30.074531335071772]
[null,"Max of Total energy use (ekWh/ft2)3",39.231785318252385]
[null,"Average of implementation cost ($/ft2)",0.17336182076768705]
[null,"Min of Savings as % of Total Electric Usage",3.931630891363282E-3]
[null,"Average of Savings as % of Total Electric Usage2",2.536621255567641E-2]
[null,"Max of Savings as % of Total Electric Usage3",4.9322187289683683E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",1.5858823529411765E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.25090584006338051]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.90132372767104807]
[null,"Min of Savings as % of Total Energy Cost",1.1918834262087652E-2]
[null,"Average of Savings as % of Total Energy Cost2",6.2100846279963741E-2]
[null,"Max of Savings as % of Total Energy Cost3",0.12410313919348988]
[null,"Average of C.Op Project Simple Payback (with incentives)",1.6666666666666667]
["courthouse","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",103292]
[null,"Average of building size (ft2)3",103292]
[null,"Max of building size (ft2)4",103292]
[null,"Min of annual electricity cost ($/ft2)",0.96978350268508395]
[null,"Average of annual electricity cost ($/ft2)2",0.96978350268508395]
[null,"Max of annual electricity cost ($/ft2)3",0.96978350268508395]
[null,"Min of annual fuel cost ($/ft2)",0.29893866417534753]
[null,"Average of annual fuel cost ($/ft2)2",0.29893866417534753]
[null,"Max of annual fuel cost ($/ft2)3",0.29893866417534753]
[null,"Min of annual energy cost ($/ft2)",1.2687221668604316]
[null,"Average of annual energy cost ($/ft2)2",1.2687221668604316]
[null,"Max of annual energy cost ($/ft2)3",1.2687221668604316]
[null,"Min of annual electricity use (kWh/ft2)",11.920969544986894]
[null,"Average of annual electricity use (kWh/ft2)2",11.920969544986894]
[null,"Max of annual electricity use (kWh/ft2)3",11.920969544986894]
[null,"Min of annual fuel use (MJ/ft2)",31.245284653458167]
[null,"Average of annual fuel use (MJ/ft2)2",31.245284653458167]
[null,"Max of annual fuel use (MJ/ft2)3",31.245284653458167]
[null,"Min of Total energy use (ekWh/ft2)",20.600215282058606]
[null,"Average of Total energy use (ekWh/ft2)2",20.600215282058606]
[null,"Max of Total energy use (ekWh/ft2)3",20.600215282058606]
[null,"Average of implementation cost ($/ft2)",0.7372798133153865]
[null,"Min of Savings as % of Total Electric Usage",5.1732226132517295E-2]
[null,"Average of Savings as % of Total Electric Usage2",5.1732226132517295E-2]
[null,"Max of Savings as % of Total Electric Usage3",5.1732226132517295E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0.14562860380734102]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.14562860380734102]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.14562860380734102]
[null,"Min of Savings as % of Total Energy Cost",8.1102568956257309E-2]
[null,"Average of Savings as % of Total Energy Cost2",8.1102568956257309E-2]
[null,"Max of Savings as % of Total Energy Cost3",8.1102568956257309E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",8.6]
["library","Count of building size (ft2)",1]
[null,"Min of building size (ft2)2",330009]
[null,"Average of building size (ft2)3",330009]
[null,"Max of building size (ft2)4",330009]
[null,"Min of annual electricity cost ($/ft2)",1.6450551348599585]
[null,"Average of annual electricity cost ($/ft2)2",1.6450551348599585]
[null,"Max of annual electricity cost ($/ft2)3",1.6450551348599585]
[null,"Min of annual fuel cost ($/ft2)",0.30598256411188784]
[null,"Average of annual fuel cost ($/ft2)2",0.30598256411188784]
[null,"Max of annual fuel cost ($/ft2)3",0.30598256411188784]
[null,"Min of annual energy cost ($/ft2)",1.9510376989718463]
[null,"Average of annual energy cost ($/ft2)2",1.9510376989718463]
[null,"Max of annual energy cost ($/ft2)3",1.9510376989718463]
[null,"Min of annual electricity use (kWh/ft2)",23.638364408243412]
[null,"Average of annual electricity use (kWh/ft2)2",23.638364408243412]
[null,"Max of annual electricity use (kWh/ft2)3",23.638364408243412]
[null,"Min of annual fuel use (MJ/ft2)",17.614671115030195]
[null,"Average of annual fuel use (MJ/ft2)2",17.614671115030195]
[null,"Max of annual fuel use (MJ/ft2)3",17.614671115030195]
[null,"Min of Total energy use (ekWh/ft2)",28.53132860686291]
[null,"Average of Total energy use (ekWh/ft2)2",28.53132860686291]
[null,"Max of Total energy use (ekWh/ft2)3",28.53132860686291]
[null,"Average of implementation cost ($/ft2)",2.5755895495613031E-2]
[null,"Min of Savings as % of Total Electric Usage",3.2418679293971325E-2]
[null,"Average of Savings as % of Total Electric Usage2",3.2418679293971325E-2]
[null,"Max of Savings as % of Total Electric Usage3",3.2418679293971325E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",0.32410115258902461]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",0.32410115258902461]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.32410115258902461]
[null,"Min of Savings as % of Total Energy Cost",8.5274228264257762E-2]
[null,"Average of Savings as % of Total Energy Cost2",8.5274228264257762E-2]
[null,"Max of Savings as % of Total Energy Cost3",8.5274228264257762E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",0.2]
["Specialty shop / space","Count of building size (ft2)",3]
[null,"Min of building size (ft2)2",131000]
[null,"Average of building size (ft2)3",224333.33333333334]
[null,"Max of building size (ft2)4",402000]
[null,"Min of annual electricity cost ($/ft2)",1.1233317910447762]
[null,"Average of annual electricity cost ($/ft2)2",1.3668305533944238]
[null,"Max of annual electricity cost ($/ft2)3",1.7832285714285714]
[null,"Min of annual fuel cost ($/ft2)",0.20957462686567163]
[null,"Average of annual fuel cost ($/ft2)2",0.35751748921694687]
[null,"Max of annual fuel cost ($/ft2)3",0.49161142857142859]
[null,"Min of annual energy cost ($/ft2)",1.3329064179104479]
[null,"Average of annual energy cost ($/ft2)2",1.7243480426113706]
[null,"Max of annual energy cost ($/ft2)3",2.2748400000000002]
[null,"Min of annual electricity use (kWh/ft2)",13.091984732824427]
[null,"Average of annual electricity use (kWh/ft2)2",17.804611352542992]
[null,"Max of annual electricity use (kWh/ft2)3",25.663142857142859]
[null,"Min of annual fuel use (MJ/ft2)",21.056218905472637]
[null,"Average of annual fuel use (MJ/ft2)2",33.581538617345842]
[null,"Max of annual fuel use (MJ/ft2)3",47.78]
[null,"Min of Total energy use (ekWh/ft2)",20.507656163626315]
[null,"Average of Total energy use (ekWh/ft2)2",27.132816524027948]
[null,"Max of Total energy use (ekWh/ft2)3",38.935365079365077]
[null,"Average of implementation cost ($/ft2)",0.23872548672962179]
[null,"Min of Savings as % of Total Electric Usage",1.1969913413603102E-2]
[null,"Average of Savings as % of Total Electric Usage2",1.6384346447068897E-2]
[null,"Max of Savings as % of Total Electric Usage3",2.5115178432355154E-2]
[null,"Min of Savings as % of Total Gas / Fuel Usage",2.6935708716300827E-2]
[null,"Average of Savings as % of Total Gas / Fuel Usage2",7.5740541490354182E-2]
[null,"Max of Savings as % of Total Gas / Fuel Usage3",0.1332535885167464]
[null,"Min of Savings as % of Total Energy Cost",1.6610912293201753E-2]
[null,"Average of Savings as % of Total Energy Cost2",3.2822485543640353E-2]
[null,"Max of Savings as % of Total Energy Cost3",4.0949981061092183E-2]
[null,"Average of C.Op Project Simple Payback (with incentives)",4.833333333333333]
["Total Count of building size (ft2)",null,512]
["Total Min of building size (ft2)2",null,26302]
["Total Average of building size (ft2)3",null,147669.11532343749]
["Total Max of building size (ft2)4",null,811821]
["Total Min of annual electricity cost ($/ft2)",null,0.22650623381709784]
["Total Average of annual electricity cost ($/ft2)2",null,1.2136232161191642]
["Total Max of annual electricity cost ($/ft2)3",null,6.7244979379046175]
["Total Min of annual fuel cost ($/ft2)",null,0]
["Total Average of annual fuel cost ($/ft2)2",null,0.65232632093497966]
["Total Max of annual fuel cost ($/ft2)3",null,4.3701285723802545]
["Total Min of annual energy cost ($/ft2)",null,0.43464077791131439]
["Total Average of annual energy cost ($/ft2)2",null,1.8659495370541448]
["Total Max of annual energy cost ($/ft2)3",null,9.6995536606488564]
["Total Min of annual electricity use (kWh/ft2)",null,3.1158008449237062]
["Total Average of annual electricity use (kWh/ft2)2",null,18.021696084148452]
["Total Max of annual electricity use (kWh/ft2)3",null,97.496836488686014]
["Total Min of annual fuel use (MJ/ft2)",null,0]
["Total Average of annual fuel use (MJ/ft2)2",null,60.21016534225199]
["Total Max of annual fuel use (MJ/ft2)3",null,508.60035973619347]
["Total Min of Total energy use (ekWh/ft2)",null,6.7451425183894695]
["Total Average of Total energy use (ekWh/ft2)2",null,34.746742012551785]
["Total Max of Total energy use (ekWh/ft2)3",null,219.20503778710426]
["Total Average of implementation cost ($/ft2)",null,0.27425218587464778]
["Total Min of Savings as % of Total Electric Usage",null,0]
["Total Average of Savings as % of Total Electric Usage2",null,6.2563555697286874E-2]
["Total Max of Savings as % of Total Electric Usage3",null,0.32264004247707534]
["Total Min of Savings as % of Total Gas / Fuel Usage",null,-6.2473091989838712E-2]
["Total Average of Savings as % of Total Gas / Fuel Usage2",null,0.12486225825586973]
["Total Max of Savings as % of Total Gas / Fuel Usage3",null,0.90132372767104807]
["Total Min of Savings as % of Total Energy Cost",null,0]
["Total Average of Savings as % of Total Energy Cost2",null,9.6829229703309622E-2]
["Total Max of Savings as % of Total Energy Cost3",null,0.49793717006903193]
["Total Average of C.Op Project Simple Payback (with incentives)",null,2.0841796874999989]

{"sheet":"Implementation results","index":1,"n_rows":22,"n_cols":35,"rows_kept":22,"cut":false,"hidden":false,"merged":[[3,24,3,34],[1,1,1,34],[4,15,4,23],[5,21,5,23],[6,21,6,23],[3,6,3,23],[4,25,4,33],[5,28,5,30],[6,28,6,30],[5,31,5,33],[6,31,6,33],[6,9,6,11],[5,25,5,27],[5,15,5,17],[6,15,6,17],[5,12,5,14],[6,12,6,14],[4,6,4,14],[6,25,6,27],[4,3,4,5],[5,18,5,20],[6,18,6,20],[6,3,6,5],[5,6,5,8],[6,6,6,8],[5,9,5,11]]}
[]
[null,"Continuous Optimization Program Results - Buildings Completed Implementation Phase"]
[]
[null,"Results to June 2020",null,null,null,null,"Before Continuous Optimization",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Results After Implementation"]
[null,"Building Type","Sample Size","Size",null,null,"Annual Utility Cost",null,null,null,null,null,null,null,null,"Annual Energy Consumption",null,null,null,null,null,null,null,null,"Implement. Cost","Energy Savings",null,null,null,null,null,null,null,null,"Simple Payback"]
[null,null,null,null,null,null,"electricity",null,null,"fuel",null,null,"total",null,null,"electricity",null,null,"fuel",null,null,"total",null,null,null,"electricity",null,null,"fuel",null,null,"total"]
[null,null,null,"(ft2)",null,null,"($/ft2.yr)",null,null,"($/ft2.yr)",null,null,"($/ft2.yr)",null,null,"(kWh/ft2.yr)",null,null,"(MJ/ft2.yr)",null,null,"(eKWh/ft2.yr)",null,null,"($/ft2)","(% kWh)",null,null,"(% GJ)",null,null,"(% $)",null,null,"years"]
[null,null,null,"min","avg","max","min","avg","max","min","avg","max","min","avg","max","min","avg","max","min","avg","max","min","avg","max","avg","min","avg","max","min","avg","max","min","avg","max","avg"]
[null,"extended care",15,40181,71593.53333333334,185656,0.65666298322291217,1.024847848418913,1.5754390872579775,0.15297620236977241,1.1819809512039514,2.5013065876906997,1.5870769230769231,2.2068287996228642,3.3657698912421292,10.692307692307692,16.058308162483705,43.051012048674245,7.1332947029791995,107.48426744466643,159.42858564993404,30.295353335723028,45.915049119335478,58.2,0.43322526956889135,2.3621137741842335E-3,5.2471666464693929E-2,0.11900740332391782,0,0.11729995854328325,0.29441857828168888,1.3534824673545005E-2,0.10022053429546232,0.20685405792956582,2.6333333333333333]
[null,"Food retail (e.g. supermarkets, grocery stores)",21,102024,133211.33333333334,155623,0.58202258471212664,2.5517098353783112,3.8551166097633156,0.11184343237816551,0.42267326578840808,0.79503260243701268,0.69386601709029216,2.9743831011667199,4.2181479583366412,6.0936697433343188,39.48515599516486,70.784400060632748,11.302862390461812,44.293254024780978,78.368168367912546,9.2333537406848212,51.788837668715132,80.372554539395651,2.4078703681816103E-2,1.1463821413195763E-2,5.6274064732305111E-2,0.16130808062893404,0,3.0772190475604443E-2,0.13191723758047302,2.4560292708493744E-2,7.4583924237362528E-2,0.20070255100939305,0.23809523809523814]
[null,"hospital",68,29819,218148.7794117647,811821,0.25703110448873162,1.3161896867287599,5.3294250882686027,0.1651672129764222,1.2902436367815315,4.3701285723802545,0.51667786892547396,2.606433323510291,9.6995536606488564,3.5556779256116027,19.412138247043341,77.927160082606093,18.649999999999999,117.42631312278638,508.60035973619347,11.649197441386093,52.030558558928448,219.20503778710426,0.26054171403835602,0,4.1181213205640999E-2,0.14813239854708757,4.9468216670789022E-3,9.066067212986173E-2,0.31667184919519076,6.7391355580504334E-3,6.6743117716519765E-2,0.1703703999363711,1.8955882352941174]
[null,"large hotel",7,150000,338025.42857142858,550000,0.72627272727272729,1.2514461731001951,1.9523518518518519,0.32241956521739129,0.72382946278382021,1.3758191269841269,1.46224,1.9752756358840153,3.3281709788359786,11.102008731970185,19.970805654507359,30.394179894179896,18.95,38.660203624547144,72.577777777777783,21.548698780702114,30.709751105770462,50.554673721340393,0.21324879370805752,2.0417405416933248E-2,4.4870162979035733E-2,6.9218649781477001E-2,4.1769457323652059E-2,0.10242690339383428,0.17795800977854473,6.1060497993974491E-2,8.2685247299915096E-2,0.10820267172086204,1.3714285714285714]
[null,"large non-food retail",1,113975,113975,113975,1.7620370256635227,1.7620370256635227,1.7620370256635227,0.173105593331871,0.173105593331871,0.173105593331871,1.9351426189953937,1.9351426189953937,1.9351426189953937,27.919806975213863,27.919806975213863,27.919806975213863,16.360078964685236,16.360078964685236,16.360078964685236,32.464273354293098,32.464273354293098,32.464273354293098,0.13487763529667465,5.9979070819820499E-2,5.9979070819820499E-2,5.9979070819820499E-2,4.5048910245409302E-2,4.5048910245409302E-2,4.5048910245409302E-2,8.5430502319067347E-2,8.5430502319067347E-2,8.5430502319067347E-2,1.8]
[null,"large office",68,54055,232280.84941176471,659725,0.66210857007735702,1.497566686325607,5.8173224478054832,0,0.500832977095229,1.5774078684674104,0.86165595693645558,1.9983996634208376,6.0249962954309781,10.114865850862016,23.626894666104956,94.703123949675259,0,41.720926662988632,189.78978273634763,13.670750002005567,35.216040961379576,100.30036833458554,0.26874653731093262,1.3851578240429818E-3,4.5387547558809534E-2,0.17878913847332015,0,0.13252478730527548,0.53364269141531318,8.7111676346305553E-3,7.1152241661496529E-2,0.27100000000000002,2.2014705882352943]
[null,"large school",112,50386,108310.09355357142,177348,0.24998987179170476,0.62684275895712815,3.254813984226653,8.3134068485200233E-2,0.4572687085322375,2.052551895224545,0.49436749769159744,1.0841114674893653,3.9975509349354734,3.1158008449237062,7.3038790511964438,32.502371310787638,9.3035403366221701,41.471146824034903,117.28867972711686,8.1045373388975701,18.823642057872807,65.082560123875652,0.19371656975432722,0,6.7142677024132819E-2,0.25023512024721217,8.0188679245283018E-3,0.11551776452071758,0.49437416666666667,4.0054839014576349E-3,9.8611174636920276E-2,0.49793717006903193,2.2178571428571439]
[null,"medium office",39,46364,74189.512820512828,149194,0.80895482263867491,1.5744488510973067,6.7244979379046175,0,0.3433795262494424,1.5046837529653174,0.99474005960416723,1.917828377346749,7.0513002826967561,9.2972643439751099,21.501953405975428,97.496836488686014,0,27.767388597213564,97.327539001637618,14.687785674056338,29.21511690520143,109.20787933920482,0.31090854177307403,1.0929025751543897E-2,6.9194661685312575E-2,0.1820978465813238,0,0.12182506664533342,0.43228269875004499,1.3828812926753897E-2,9.8895845326325116E-2,0.26393303770524174,2.2256410256410257]
[null,"museum",1,311803,311803,311803,1.0423248012366784,1.0423248012366784,1.0423248012366784,0,0,0,1.0423248012366784,1.0423248012366784,1.0423248012366784,19.082561745717648,19.082561745717648,19.082561745717648,0,0,0,19.082561745717648,19.082561745717648,19.082561745717648,0.31818249999999998,8.9120039976558943E-2,8.9120039976558943E-2,8.9120039976558943E-2,"n/a","n/a","n/a",9.6719576000000002E-2,9.6719576000000002E-2,9.6719576000000002E-2,2.2000000000000002]
[null,"recreation",22,49000,115913.81818181818,512000,0.41265327866206053,1.8768337481078115,3.9490348817228935,0.34751400489224038,1.3113707595994506,3.8222277227722774,0.76016728355430097,3.1882045077072623,7.6340099009900992,7.722448979591837,25.232783731390807,49.335726072607258,26.423705472508313,117.4221838749787,355.49504950495049,15.412110095889968,57.850057029995995,148.08435093509354,0.50261072004780472,0,6.0748782367188413E-2,0.23375688630736027,0,0.10276263421098628,0.47481000000000001,0,8.9344412290834396E-2,0.36443609674315791,2.4999999999999996]
[null,"restaurant",3,26302,34962.333333333336,50000,1.5543158999475248,3.2160441007340359,5.4346399999999999,0,0.78699721182438331,1.2065399999999999,2.6591764022545816,4.0030413125584188,6.6411800000000003,17.270176666083611,43.637310328002066,75.65352,0,54.788387849105014,115.44516354731502,37.98823431792259,58.856306952753449,89.242408888888875,0.28203225313588004,1.4635778883187575E-2,6.7494114295125487E-2,0.14631795152455052,1.9116523272727275E-2,3.7600593166513888E-2,5.6084663060300494E-2,1.7047803038958764E-2,5.1891627399843571E-2,8.6487906194896949E-2,1.8666666666666665]
[null,"shopping mall",3,250000,375333.33333333331,576000,0.49362193333333332,1.2368783666666667,1.8791720000000001,6.3236666666666663E-2,0.15052200314113692,0.29368534275674413,0.55685859999999998,1.3874003698078037,1.973816,8.472461233333334,22.715824855555553,33.996679999999998,5.0933333333333337,75.066203703703692,187.64,9.8872760481481485,43.567548106584354,86.118902222222218,7.914969185349667E-2,1.955982884268704E-2,3.1647526624582124E-2,3.8362625879938869E-2,0,1.4618538324420678E-2,4.3855614973262035E-2,2.0585857518593566E-2,2.4277620426981908E-2,2.8672440149822603E-2,1.4333333333333333]
[null,"univ. / college",133,29637,124740.87614736841,580347,0.22650623381709784,1.0236844516386217,4.1744033959470714,0,0.57404537935523003,2.4616655376898207,0.44685437641504888,1.597729830993851,4.8175907980938284,4.9478380519534673,17.081806830587105,59.634334227815302,0,58.505537135849416,289.93823800847156,6.7451425183894695,33.333344923878606,105.21072022819941,0.34412509051723644,5.857102922350205E-4,8.5382540256367837E-2,0.32264004247707534,-6.2473091989838712E-2,0.16731591849176014,0.78629032286453093,1.1677322430375107E-2,0.13606124611834766,0.38363098324392464,2.1045112781954884]
[null,"Overall",493,null,153360.2171310345,null,null,1.2713881518292971,null,null,0.64724147049840153,null,null,1.9186296223276986,null,null,19.417338698422558,null,null,60.771172196585248,null,null,36.299570334633941,null,0.23699912853687835,null,4.6867251029112593E-2,null,null,9.5871998289864632E-2,null,null,7.340943956896355E-2,null,1.6815609405465235]

{"sheet":"Implementation summary for web","index":2,"n_rows":22,"n_cols":15,"rows_kept":22,"cut":false,"hidden":false,"merged":[[1,1,1,14],[4,4,4,6],[4,7,4,9],[3,4,3,9],[3,10,3,14],[4,11,4,13]]}
[]
[null,"Continuous Optimization Program Results - Buildings Completed Implementation Phase"]
[]
[null,"Results to June 2020",null,null,"Before Continuous Optimization",null,null,null,null,null,"Results After Implementation"]
[null,"Building Type","Sample Size","Size","Annual Utility Cost",null,null,"Annual Energy Consumption",null,null,"Implement. Cost","Energy Savings",null,null,"Simple Payback"]
[null,null,null,null,"electricity","fuel","total","electricity","fuel","total",null,"electricity","fuel","total"]
[null,null,null,"(ft2)","($/ft2.yr)","($/ft2.yr)","($/ft2.yr)","(kWh/ft2.yr)","(MJ/ft2.yr)","(eKWh/ft2.yr)","($/ft2)","(% kWh)","(% GJ)","(% $)","years"]
[null,null,null,"avg","avg","avg","avg","avg","avg","avg","avg","avg","avg","avg","avg"]
[null,"large school",112,108310.09355357142,0.62684275895712815,0.4572687085322375,1.0841114674893653,7.3038790511964438,41.471146824034903,18.823642057872807,0.19371656975432722,6.7142677024132819E-2,0.11551776452071758,9.8611174636920276E-2,2.2178571428571439]
[null,"shopping mall",3,375333.33333333331,1.2368783666666667,0.15052200314113692,1.3874003698078037,22.715824855555553,75.066203703703692,43.567548106584354,7.914969185349667E-2,3.1647526624582124E-2,1.4618538324420678E-2,2.4277620426981908E-2,1.4333333333333333]
[null,"medium office",39,74189.512820512828,1.5744488510973067,0.3433795262494424,1.917828377346749,21.501953405975428,27.767388597213564,29.21511690520143,0.31090854177307403,6.9194661685312575E-2,0.12182506664533342,9.8895845326325116E-2,2.2256410256410257]
[null,"univ. / college",133,124740.87614736841,1.0236844516386217,0.57404537935523003,1.597729830993851,17.081806830587105,58.505537135849416,33.333344923878606,0.34412509051723644,8.5382540256367837E-2,0.16731591849176014,0.13606124611834766,2.1045112781954884]
[null,"large hotel",7,338025.42857142858,1.2514461731001951,0.72382946278382021,1.9752756358840153,19.970805654507359,38.660203624547144,30.709751105770462,0.21324879370805752,4.4870162979035733E-2,0.10242690339383428,8.2685247299915096E-2,1.3714285714285714]
[null,"large office",68,232280.84941176471,1.497566686325607,0.500832977095229,1.9983996634208376,23.626894666104956,41.720926662988632,35.216040961379576,0.26874653731093262,4.5387547558809534E-2,0.13252478730527548,7.1152241661496529E-2,2.2014705882352943]
[null,"recreation",22,115913.81818181818,1.8768337481078115,1.3113707595994506,3.1882045077072623,25.232783731390807,117.4221838749787,57.850057029995995,0.50261072004780472,6.0748782367188413E-2,0.10276263421098628,8.9344412290834396E-2,2.4999999999999996]
[null,"hospital",68,218148.7794117647,1.3161896867287599,1.2902436367815315,2.606433323510291,19.412138247043341,117.42631312278638,52.030558558928448,0.26054171403835602,4.1181213205640999E-2,9.066067212986173E-2,6.6743117716519765E-2,1.8955882352941174]
[null,"restaurant",3,34962.333333333336,3.2160441007340359,0.78699721182438331,4.0030413125584188,43.637310328002066,54.788387849105014,58.856306952753449,0.28203225313588004,6.7494114295125487E-2,3.7600593166513888E-2,5.1891627399843571E-2,1.8666666666666665]
[null,"extended care",15,71593.53333333334,1.024847848418913,1.1819809512039514,2.2068287996228642,16.058308162483705,107.48426744466643,45.915049119335478,0.43322526956889135,5.2471666464693929E-2,0.11729995854328325,0.10022053429546232,2.6333333333333333]
[null,"large non-food retail",1,113975,1.7620370256635227,0.173105593331871,1.9351426189953937,27.919806975213863,16.360078964685236,32.464273354293098,0.13487763529667465,5.9979070819820499E-2,4.5048910245409302E-2,8.5430502319067347E-2,1.8]
[null,"museum",1,311803,1.0423248012366784,0,1.0423248012366784,19.082561745717648,0,19.082561745717648,0.31818249999999998,8.9120039976558943E-2,"n/a",9.6719576000000002E-2,2.2000000000000002]
[null,"Food retail (e.g. supermarkets, grocery stores)",21,133211.33333333334,2.5517098353783112,0.42267326578840808,2.9743831011667199,39.48515599516486,44.293254024780978,51.788837668715132,2.4078703681816103E-2,5.6274064732305111E-2,3.0772190475604443E-2,7.4583924237362528E-2,0.23809523809523814]
[null,"Overall",493,153360.2171310345,1.2713881518292971,0.64724147049840153,1.9186296223276986,19.417338698422558,60.771172196585248,36.299570334633941,0.23699912853687835,4.6867251029112593E-2,9.5871998289864632E-2,7.340943956896355E-2,1.6815609405465235]